## Sheet1
OS Violation ID | Remedial Action ID | Begin date/time UTC | End date/time UTC | Type of OS violation | Affected network element (in case of congestion only) | Contingency (in case of congestion only) | Location | Time of identification | Time of activation of RA | Begin RA / time UTC | End RA / time UTC | Entity which first identified the violation | Entity which decided on remedial action | Entities which were consulted and agreed with the RA | Maximum overload between beginning and end time (if applicable), % Fmax | Maximum overload between beginning and end time (if applicable), MVA | % of flow on network element coming from cross-border exchanges (if applicable), % Fmax | % of flow on network element coming from renewables generation (if applicable), % Fmax | TSOs involved in Remedial Action | Type of Remedial Action | Maximum redispatch/countertrading power (if applicable) | Share of redispatching handled through demand response | Total redispatch/countertrading energy (if applicable) | Total cost (in case of redispatching and countertrading) | Incl. cost of renewables curtailment (if applicable) | Calculated overload if no RA applied (in case of congestion only) | Remaining maximum overload after remedial action | In case of remaining overload, number of hours | In case of remaining overload, was there a later coordination addressing this | In case of cross-regional RDPCH, existance of contradicting objectives and between which regions
1 | 1 |  |  | Thermal limits : violation of 20 min overload | Line NODE1 NODE2 | Line NODE1 NODE2 | TENNET DE | DA |  |  |  | TENNET DE |  |  | 135% | 50 | 5% | 10% | TENNET DE | internal RDPCH | 500 | 10% | 2300 | 230000 | 100000 | 139% | 0% | - | - | -
2 | 2 |  |  | Thermal limits | Line NODE3 NODE4 | Transformer NODE61 NODE62 | TENNET DE | DA |  |  |  | CORESO |  |  | 135% | 50 | 15% | 15% | TENNET DE, 50 HZ | internal RDPCH | 400 | 0% | 1700 | 145000 | 0 | 139% | 5% | 2 | Yes | -
3 | 3 |  |  | Voltage limits | - | - | RTE | ID H-12 |  |  |  | CORESO | RTE | - | - | - | - | - | RTE | TOPOLOGY CHANGE | - | - | - | - | 0 | - | - | - | - | -
4 | 4 |  |  | Thermal limits | Line NODE5 NODE6 | TR NODE71 NODE72 | PSE | REAL TIME |  |  |  | TSC NET | PSE |  | 122% | 75 | 75% | 50% | PSE, 50 HZ | TOPOLOGY CHANGE | - | - | - | - | 0 | 122% | 0% | - | - | -
5 | 5 |  |  | Thermal limits | Line NODE6 NODE7 | Line NODE22 NODE23 | TENNET DE | ID H-12 |  |  |  | TSC NET |  |  | 112% | 176 | 75% | 50% | TENNET DE, RTE, TERNA | cross-regional RDPCH | 300 | 0% | 900 | 245000 | 0 | 119% | 0% | - | - | TSC/CORESO
6 | 6 |  |  | Thermal limits | Line NODE8 NODE9 | Line NODE32 NODE33 | TERNA | ID H-12 |  |  |  | CORESO | TERNA | [6 empty] | regional RDPCH | 400 | 0% | 800 | 545000 | 0 | 126% | 0% | - | - | -
7 | 7 |  |  | Thermal limits | Line NODE10 NODE21 | Line NODE42 NODE43 | 50Hz | ID H-12 |  |  |  | 50Hz | 50Hz | [6 empty] | internal RDPCH | 150 | 0% | 450 | 45000 | 0 | 110% | 0% | - | - | -